## Slide 1: Operation and Maintenance of Biofiltration and RO Systems
Dr. Babak Roshani, Ph.D., P.Eng.
&
Dillon Petrucha, P.Eng.
Service@dropwater.ca

## Slide 2: Definition
Biological filtration is defined by AWWA Committee as:
“The operational practice of managing, maintaining,
and promoting biological activity on granular media in a filter to enhance the removal of organic and inorganic constituents before treated water is introduced into the distribution system” (Brown et al.2016).
In the presence of :
No oxidant residuals,
Indigenous organisms attach on the filter media surface and form a biofilm.

## Slide 3: Biofilm
Once established, the quantity of biomass maintained within the biofilm matrix tends to remain consistent over time,
and the biomass is resilient to varying temperatures, backwashing, substrate loading rates, and in some cases, low concentrations (e.g.,<0.1 mg/L free chlorine) of filter influent oxidant residuals (Evans et al. 2013a, Hooper et al. 2019, Lauderdale et al. 2018, Pharand et al. 2014).

## Slide 4: Removal Mechanisms
Physical separation (i.e., particle removal by Sand)
Adsorption (DOC removal by GAC)
Biodegradation/biotransformation (Fe, Mn, NH3)

## Slide 5
Effluent Concentration as a Function of Time Comparing Removal Trends Using an Inert Filter Media (e.g., Sand, Anthracite) and Fresh Adsorptive Media (e.g., GAC) from Start‐Up. Adapted from Brown et al. 2018.

## Slide 6
Illustration of Contaminant Removal Mechanisms by Biological Filtration with a Porous Media.

## Slide 7
Iron and Manganese
  Soluble
  Insoluble

## Slide 8
Iron
Manganese
Source: http://edafologia.ugr.es
Pourbaix Diagrams for Fe & Mn

## Slide 9: Pourbaix Diagram (Electrode potential/ PH diagram)
Source: http://edafologia.ugr.es

## Slide 10: Pourbaix Diagram of Nitrogen
Source: http://edafologia.ugr.es

## Slide 11
Iron and Manganese Removal
Chemical Oxidation of Iron
Ferrous
Ferric
The stoichiometric dosing rates
Chemical Oxidation of Manganese
Mn(II)
Mn(IV)

## Slide 12
Conventional Iron and Manganese Removal
How long does it take?

## Slide 13
Conventional Iron and Manganese Removal
Intense aeration just for Iron removal
Special media
    Manganese Greensand
    Greensand Plus
    Pyrolusite
Chemical oxidation (Cl2, KMnO4, O3)
    Chemical injection
Adsorption (Resin)

## Slide 14
Conventional Iron and Manganese Removal
Expense of chemical consumption
Frequent need for backwash : 18-24 hours
Storage and handling of strong oxidant
Limited filtration rates: Approximately 2.6USGPM/ft2. of media
Time-consuming operation and maintenance
Limitations

## Slide 15
Conventional Iron and Manganese Removal
Chemical feed pump maintenance, KMnO4 make down
Oxidant carry over
  Resulting in ‘pink water’ to reservoir
  Possible damage to Membrane elements downstream
Loss of media bed due to frequent backwashing
No Ammonia or DOC removal
Limitations

## Slide 16
Conventional Ammonia Removal
Break-point chlorination in Distribution Systems
Chlorine to NH3-N ratio is 10:1
Toxic disinfection by-Products

## Slide 17
Conventional Ammonia Removal
Limitations
Chlorine : NH3-N ratio is 10:1
Toxic disinfection by-Products
Deterioration of valves and fittings in distribution systems

## Slide 18
Breakpoint Chlorination Curve

## Slide 19: Nutritional Balance

## Slide 20: Nutritional Balance

## Slide 21: Nutritional Balance

## Slide 22: Nutritional Balance

## Slide 25: Biofilm is Predominately Extracellular Polymeric Substances (EPS)
EPS Benefits bacteria
Adhesion
Protection
Storage
Excess EPS impairs filter performance
Head loss
Clogging

## Slide 28: Bacterial Growth

## Slide 29: Biofilter Performance Drivers and Their Impact

## Slide 30: Water Quality Monitoring
Temperature
pH
Turbidity
Iron
Manganese
Ammonia

## Slide 31: Recommended Biofilter Monitoring During Routine Operations

## Slide 32: Optimization Strategies
Biofiltration optimization leverages design and operational strategies to enhance contaminant biodegradation kinetics, particle removal, and/or filter hydraulics. Biofilter optimization strategies that have been explored in drinking water treatment and will be discussed in this section include:
Media selection
Backwash protocol
Nutrient augmentation
pH adjustment

## Slide 33: Backwashing and Air Scour Frequency
*Backwashing depends on differential pressure for each filter
Week

## Slide 34: Operation and Maintenance
  Monitoring
  Start‐Up and Acclimation
  Steady‐State Operation
  Shutdown, Idling, and Restart

## Slide 35: Operation and Maintenance of Reverse Osmosis System

## Slide 36: Reverse Osmosis
Topics for Reverse Osmosis Systems:
  Fundamentals
  Operation
  Maintenance

## Slide 37: Filtration Spectrum

## Slide 38: Filtration Spectrum Types

## Slide 39: Typical Flow Types

## Slide 40: Basic Reverse Osmosis Principle

## Slide 41: The Spiral Wound Membrane
Feedwater Inlet
Permeate Outlet
Concentrate Outlet
Permeate Outlet
Fiberglass Outerwrap
Membrane
Permeate Carrier
Spacer

## Slide 42: Typical Reverse Osmosis Equipment

## Slide 43: One Stage RO System

## Slide 44: 2 Stages RO system

## Slide 45: RO System for Saline Water

## Slide 46: RO Skid with Antiscalant

## Slide 47
1. Bio-organic Fouling
The Issues...
Molecular Adsorption
2. Physico-Chemical Integrity
De-lamination
PA
PS
Flux loss
Solute passage

## Slide 48
Cartridge Filter

## Slide 49
Membrane Scaling

## Slide 50
RO Direct Feed without Pre-treatment

## Slide 51
RO Direct Feed without Pre-treatment

## Slide 52
Membrane Fouling

## Slide 53
Membrane Biofouling

## Slide 54
Membrane fouling is referred to as the deposition or adsorption of the particles
contained in the feed stream on the membrane surface or in the membrane pores
This gel layer forms a secondary barrier to flow through the membrane
Membrane fouling has a negative impact on filtration performance as it decreases the permeate flux
↓ flux
↓ membrane life
↑ energy use
Membrane Fouling
Schematics of membrane fouling mechanisms: (A) pore blockage, (B) pore
constriction, (C) intermediate blockage and (D) cake filtration.

## Slide 55
Membrane
Cleaning chemicals (if needed)
Filtrate Tank
Cleaning in Backwash Mode

## Slide 56
Cleaning in Forward Flush Mode
Pump
Feed
Membrane
Concentrate

## Slide 57: Operation Overview
  Check correct setting of all valves
  Purge feed water
  Purge system at low pressure
  Partially close feed pressure control valve
  Ramp up or start high pressure pump
  Slowly open feed control valve or adjust pump speed
  Slowly close concentrate control valve to adjust to design recovery
  Check all chemical dosages rates
  Let system stabilize (1 hour)
  Record all operating parameters
  Check permeate conductivity
  Take water samples and analyze
  Compare performance to prediction
  Record operating data daily (recommended)
  Flush with permeate to shut down

## Slide 58: Monitoring Reverse Osmosis Numbers
Main parameters affecting operation:
  Temperature
  Recovery
  Pressure
  Flow
  Salt Rejection (Conductivity)
  and sometimes pH

## Slide 59: How to Monitor Reverse Osmosis Performance
Parameters affecting operation
  Normalized Parameters
    Permeate Flow
    Differential Pressure
    Salt Rejection
  Overall vs per Stage Performance

## Slide 60: Normalized Parameters
Why?
  Fluctuation in operating conditions cause permeate flow and salt passage changes
  Detecting performance changes from membrane properties
  Eliminating effects of fluctuating operating conditions gives a better perspective of membrane health

## Slide 61: Reverse Osmosis Maintenance
What determines membrane health?
  Normalized flow declines by 10%
  Pressure drop increases by 10-15%
  Normalized salt passage increases by 5-10%
    Depending on system design

## Slide 62: Normalized Permeate Flow
The main parameter of importance
  Cleaning after 10-15% decline maximizes performance
  Waiting too long reduces performance and lifespan

## Slide 63: Normalized Permeate Flow

## Slide 64: Membrane Health Degradation
Scale
  Effects the backend of the system
  Mineral build up
  Lower permeate flow, higher pressure, higher salt passage
Fouling
  Effects the frontend of the system
  Organic material build up
  higher pressure, lower permeate flow, lower salt passage
Oxidation
  Effects the whole system but starts at frontend
  lower pressure, lower permeate flow, higher salt passage

## Slide 65: General Membrane Cleaning Guidelines
    Determine location of fouling or scaling
    Obtain detailed feed water source analysis
    Identify pH and temperature limits of membrane element
    Permeate flush between cleanings
    Permeate for cleaning chemical solution preparation
    Inspect CIP tank prior to each cleaning
    Measure pH during cleaning: adjust pH when needed
    Typical cleaning pH limits 3.5 – 10
    Harsh cleaning pH limits 2 - 12
    Chemical solution preparation
    Alkaline cleanings at elevated temperatures: 35°C (95°F)
    Acid cleanings can be carried out at minimum 25°C (77°F)
    When using commercial cleaners
    Never use household cleaners

## Slide 66: Membrane Clean-in-Place System

## Slide 67: Membrane Cleaning Types
Scale
  Dissolve mineral build up with low pH
  Minerals can solidify the membrane material
    Can prevent membrane from producing permeate
    Results in need for membrane replacement
Fouling
  Break down organic material with high pH
  Organics can break down membrane
    Can behave similarly to oxidation
    repeated organic breakdown results in the need for membrane replacement
Oxidation
  This cannot be cleaned
  Severe oxidation results in membrane replacement

## Slide 68: Membrane Cleaning Types
High or Low pH Cleaning?
  BOTH
    Typically, high pH then low pH
  Monitor the membrane degradation to determine what type of cleaning is needed
    Membrane autopsies are helpful
    Feed water analysis is helpful
    Trial and error can be helpful

## Slide 69: Membrane Cleaning

## Slide 70: Membrane Autopsy

## Slide 71: Thank You & Questions? Service@dropwater.ca Systems@dropwater.ca